## Slide 1
ANNUAL MEETING 2011
AFTER FUKUSHIMA ACCIDENT
L. Antola

## Slide 2: Content
  Fukushima Accident
  ITER activity
  Emerging lessons
    NPP in Operation
    New Designs
  Participation in international follow-up
Annual Meeting December 16, 2011 - Rome

## Slide 3: Fukushima Accident
The 2011 Tohoku Earthquake Magnitude 9.0 attacked Tohoku Kano area on March 11 with serious secondary effects in particular a significant tsunami.
Annual Meeting December 16, 2011 - Rome

## Slide 4: Fukushima Accident
The 6 units in Fukushima Daiichi NPP (5 BWRs Mark I , Unit 6 Mark II) designed more than 40 years ago were affected loss of offsite power due to the seismic event
The D/G automatically started to power the Units. Unfortunately a seismic generated tsunami hit Fukushima in a series of waves, the first enormous wave (14-15 m) hit Dai-ichi at 15.27 (41 minutes after the quake)
Annual Meeting December 16, 2011 - Rome

## Slide 5: Fukushima Accident
The tsunami (14-15 m) put out of service the seawater cooling pump station, and flooded the D/G locals of all Units and the distribution panels . Causing a total loss of ac-power (SBO)
Only at Unit 6 one air cooled D/G survived as: its distribution board was not submerged, it was at higher level and the damage of the seawater pumps did not affect that D/G
The D/G of Unit 6 was cross connected to unit 5 allowing to cool both reactors and both SF pools.
Annual Meeting December 16, 2011 - Rome

## Slide 6: Fukushima Accident
Annual Meeting December 16, 2011 - Rome

## Slide 7: Fukushima Accident
When the cooling function was completely lost the reactors overheated. This resulted in:
Pressurization of primary circuit
Discharge of steam through safety relief valves to the suppression pools
Pressurization of primary containment
Need to vent and consequent several disruptive explosions because of accumulation of H2
Annual Meeting December 16, 2011 - Rome

## Slide 8: Fukushima Accident
The Fukushima accident has been very severe and
  classified at highest level 7 of INES (International Nuclear Event Scale) as Chernobyl Accident
The severe accident brought to core-melt in three units with possible expulsion of molten material
A large quantity of radioactivity has been released in the air and in the sea water
About 80.000 people were evacuated (return has not yet started).
Annual Meeting December 16, 2011 - Rome

## Slide 9: ITER Activity
  A preliminary analysis report has been issued at the end of May 2011.
  The report included a set of ‘’emerging considerations’’ from the accident in relation to operating NPP and New design
  We are reviewing the report and we expect to issue the final version in short.
Annual Meeting December 16, 2011 - Rome

## Slide 10: Emerging Considerations
  The Fukushima accident has brought at the attention of utilities, designers and regulators an extremely important set of issues which are under analysis
  While the NPP structures/systems appear to have successfully withstood the seismic event, the defense against the seism-generated tsunami has failed, due to underestimation
  This has determined a common-caused total loss of ac-power which, after a partial initial operation of steam driven reactor cooling system, has caused the loss of cooling function on four units (reactors core and spent fuel pool)
Annual Meeting December 16, 2011 - Rome

## Slide 11: Emerging Considerations
  The accident in Fukushima shows a peculiar feature:
    it has highlighted a significant number of deficiencies and weaknesses
    the issues cover a very wide spectrum of technical and organizational/management areas including responsibilities
    the lessons learned impact at the same time the activity of designers, operators and regulators.
Annual Meeting December 16, 2011 - Rome

## Slide 12: Emerging Considerations
  The indications emerging from Fukushima accident can be distinguished for ‘’new design’’ and ‘’operating NPP’’.
  While for new design it is more comfortable, in terms of time constraints, to feedback the learning from Fukushima event, the priority in the use of ‘’lessons learned’’ is for the operating NPP
  This has called for immediate review and assessment of operating NPP. In EU the prompt decision has been taken to perform the ‘’stress tests’’ according to specifications and schedule defined by ENSREG + EC
Annual Meeting December 16, 2011 - Rome

## Slide 13: Operating NPP
  The reassessment of operating NPP need to consider the safety issue related to the following topics:
    Site External Events
    Multi units site
    Spent Fuel Pool
    H2 Management
    Total Blackout
    Loss of Heat Sink
    Severe Accident Management
    Emergency preparedness
Annual Meeting December 16, 2011 - Rome

## Slide 14: Operating NPP
  In addition for Operating NPP we consider of particular relevance to reinforce the objective, scope and quality of the activities related to:
      Periodic Safety Review (PSR)
      Plant Life Extension (PLEX).
Annual Meeting December 16, 2011 - Rome

## Slide 15: New Designs
  Current new NPP designs already provide means to deal with a number of shortcomings from Fukushima accident; nevertheless the attention should be systematically devoted to all following topics.
NPP siting & E. Events (EE) Multi-unit site Seismic Hazard &Tsunami Defense in Depth Spent Fuel Pool Probabilistic Safety Analysis Accident Analysis for EE | Station Blackout Loss of Ultimate Heat Sink H2 Management Accident Management Human Factor Reliability &Habitability ECR Use of Experience
Annual Meeting December 16, 2011 - Rome

## Slide 16: Follow up activities
    Review of Reports from Japanese government and other technical data from Japanese authorities.
    Review of ITER Report
    Analysis of the results of Stress Tests in EU
    Participating to the follow-up analysis and investigation a
    SNETP research program
    IAEA ISSC EBP Working Groups for External Events
    IAEA ISSC EBP Working Group on ‘’Public Communication’’ (leadership with JNES)
    ----------
Annual Meeting December 16, 2011 - Rome